## Sheet1
Type | ConductorName | RGBColor | ActualImpedance | PosSequenceResistance_PerLUL | PosSequenceReactance_PerLUL | PosSequenceAdmittance_PerLUL | ZeroSequenceResistance_PerLUL | ZeroSequenceReactance_PerLUL | ZeroSequenceAdmittance_PerLUL | Diameter_SUL | ContinuousCurrentRating | InterruptCurrentRating | ConductorType | CableGMR_MUL | CableResistance_PerLUL | CableDiamOverInsul_SUL | CableDiamOutside_SUL | CableDiamConductor_SUL | CableConNeutStrandDiameter_SUL | CableConNeutResistance_PerLUL | CableConNeutStrandCount | DamageCurveFactor | ConductorMaterial | InsulationMaterial | JacketMaterial | MaxTemp_C | CableCoreStrandDiam_SUL | CableCoreStrandCount | CableSheathThickness_SUL | CableJacketThickness_SUL | CableConNeutRingDiameter_SUL | CableConNeutLayFactor | IsSuitableForAmpacity | Description | WinterContCurrentRating | WinterEmerCurrentRating | Is3CoreCable
1 | #6CRAPO | 0,0,255 | 1 | 12.87 | 3.811 | 1.075 | 13.243 | 6.006 | 8.683 | 0 | 18 | 18 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 25 | 0
2 | 1/0ACSR | 0,255,0 | 1 | 1.034 | 0.8641 | 4.768 | 1.555 | 2.445 | 2.478 | 0 | 210 | 309 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.94 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 278 | 309 | 0
3 | 1/0ACSR(2) - parallel | 0,255,0 | 1 | 0.517 | 0.4321 | 9.536 | 0.7775 | 1.2225 | 4.956 | 0 | 420 | 618 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.94 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 556 | 618 | 0
4 | 1/0ACSR2P | 0,0,255 | 1 | 0.56 | 0.444 | 9.056 | 1.088 | 2.02 | 3.371 | 0 | 378 | 420 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.88 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 556 | 618 | 0
5 | 1/0CN15 | 125,0,0 | 1 | 1.025 | 0.516 | 68.355 | 2.501 | 1.287 | 68.355 | 0 | 161 | 161 | ActZ | 0 | 0 | 0.845 | 1.35 | 0.362 | 0.073 | 13.9 | 13 | 4.97 | Al | XLP | PVC | 90 | 0.092 | 19 | 0.045 | 0.065 | 0.86 | 1.2 | 0 |  | 184 | 184 | 0
6 | 1/0CN25 | 0,125,0 | 1 | 1.025 | 0.516 | 68.355 | 2.501 | 1.287 | 68.355 | 0 | 163 | 163 | ActZ | 0 | 0 | 0.845 | 1.35 | 0.362 | 0.073 | 13.9 | 13 | 4.97 | Al | XLP | PVC | 90 | 0.092 | 19 | 0.045 | 0.065 | 0.86 | 1.2 | 0 |  | 186 | 186 | 0
7 | 1/0CN35 | 0,0,125 | 1 | 1.025 | 0.516 | 68.355 | 2.501 | 1.287 | 68.355 | 0 | 163 | 163 | ActZ | 0 | 0 | 0.845 | 1.35 | 0.362 | 0.073 | 13.9 | 13 | 4.97 | Al | XLP | PVC | 90 | 0.092 | 19 | 0.045 | 0.065 | 0.86 | 1.2 | 0 |  | 186 | 186 | 0
8 | 1/0CU | 255,255,0 | 1 | 0.597 | 0.7598 | 5.432 | 1.191 | 2.495 | 2.667 | 0 | 247 | 274 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.89 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 349 | 388 | 0
9 | 1/0SOLCU | 0,255,255 | 1 | 0.606 | 0.746 | 5.527 | 1.144 | 2.263 | 2.687 | 0 | 267 | 378 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.89 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 378 | 378 | 0
10 | 1/0STCU | 255,0,255 | 1 | 0.614 | 0.7531 | 5.481 | 1.207 | 2.488 | 2.681 | 0 | 240 | 267 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.89 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 340 | 378 | 0
11 | 1000CN15 | 125,125,0 | 1 | 0.272 | 0.303 | 403.15 | 0.635 | 0.213 | 403.15 | 0 | 610 | 610 | ActZ | 0 | 0 | 1.65 | 1.8 | 1.152 | 0.0808 | 8.712 | 14 | 47.04 | Al | EPR | PVC | 90 | 0.1644 | 37 | 0.045 | 0.05 | 1.7 | 1.2 | 0 |  | 695 | 695 | 0
12 | 1000CN25 | 125,125,0 | 1 | 0.272 | 0.303 | 403.15 | 0.635 | 0.213 | 403.15 | 0 | 612 | 612 | ActZ | 0 | 0 | 1.65 | 1.8 | 1.152 | 0.0808 | 8.712 | 14 | 47.04 | Al | EPR | PVC | 90 | 0.1644 | 37 | 0.045 | 0.05 | 1.7 | 1.2 | 0 |  | 698 | 698 | 0
13 | 1000CU | 125,125,0 | 0 | 0.068112 | 0.3997 | 0 | 0 | 0 | 0 | 1.151 | 1300 | 1560 | Bare | 1.151 | 6.0773 | 1.151 | 1.151 | 1.151 | 1.151 | 6.0773 | 8 | 67.5 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1300 | 1560 | 0
14 | 1000CUEPR | 0,125,125 | 1 | 0.18 | 0.33 | 500.9 | 0.6 | 0.322 | 500.9 | 0 | 760 | 760 | ActZ | 0 | 0 | 1.652 | 1.8 | 1.152 | 0.0808 | 8.712 | 14 | 74.71 | Cu | EPR | PVC | 90 | 0.128 | 61 | 0.045 | 0.06 | 1.7 | 1.2 | 0 |  | 866 | 866 | 0
15 | 1000CUEPR_SPG | 125,0,125 | 1 | 0.069 | 0.376 | 234.9 | 0.195 | 1.112 | 234.9 | 0 | 99 | 99 | ActZ | 0 | 0 | 1.652 | 1.8 | 1.152 | 0.0808 | 8.712 | 14 | 74.71 | Cu | EPR | PVC | 90 | 0.128 | 61 | 0.045 | 0.06 | 1.7 | 1.2 | 0 |  | 99 | 99 | 0
16 | 1000CUXLP | 255,0,0 | 1 | 0.18 | 0.33 | 500.9 | 0.6 | 0.322 | 500.9 | 0 | 760 | 760 | ActZ | 0 | 0 | 1.652 | 1.8 | 1.152 | 0.0808 | 8.712 | 14 | 74.71 | Cu | XLP | PVC | 90 | 0.128 | 61 | 0.045 | 0.06 | 1.7 | 1.2 | 0 |  | 866 | 866 | 0
17 | 1000CUXLP_SPG | 0,255,0 | 1 | 0.069 | 0.376 | 234.9 | 0.195 | 1.112 | 234.9 | 0 | 99 | 99 | ActZ | 0 | 0 | 1.652 | 1.8 | 1.152 | 0.0808 | 8.712 | 14 | 74.71 | Cu | XLP | PVC | 90 | 0.128 | 61 | 0.045 | 0.06 | 1.7 | 1.2 | 0 |  | 99 | 99 | 0
18 | 1033AAC | 0,125,125 | 0 | 0.11088 | 0.39864 | 0 | 0 | 0 | 0 | 1.17 | 980 | 1170 | Bare | 1.17 | 6.1776 | 1.17 | 1.17 | 1.17 | 1.17 | 6.1776 | 8 | 45.45 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 980 | 1170 | 0
19 | 1033ACSR | 125,0,125 | 0 | 0.10349 | 0.38491 | 0 | 0 | 0 | 0 | 1.246 | 1060 | 1270 | Bare | 1.246 | 6.5789 | 1.246 | 1.246 | 1.246 | 1.246 | 6.5789 | 8 | 66.11 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1060 | 1270 | 0
20 | 1113AAC | 255,0,0 | 0 | 0.10296 | 0.39283 | 0 | 0 | 0 | 0 | 1.22 | 1040 | 1240 | Bare | 1.22 | 6.4416 | 1.22 | 1.22 | 1.22 | 1.22 | 6.4416 | 8 | 48.9 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1040 | 1240 | 0
21 | 1113ACSR | 0,255,0 | 0 | 0.096624 | 0.37963 | 0 | 0 | 0 | 0 | 1.293 | 1110 | 1330 | Bare | 1.293 | 6.827 | 1.293 | 1.293 | 1.293 | 1.293 | 6.827 | 8 | 71.23 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1110 | 1330 | 0
22 | 1192AAC | 0,0,255 | 0 | 0.096624 | 0.38861 | 0 | 0 | 0 | 0 | 1.27 | 1090 | 1300 | Bare | 1.27 | 6.7056 | 1.27 | 1.27 | 1.27 | 1.27 | 6.7056 | 8 | 52.44 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1090 | 1300 | 0
23 | 1192ACSR | 125,0,0 | 0 | 0.090288 | 0.37594 | 0 | 0 | 0 | 0 | 1.338 | 1160 | 1390 | Bare | 1.338 | 7.0646 | 1.338 | 1.338 | 1.338 | 1.338 | 7.0646 | 8 | 76.28 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1160 | 1390 | 0
24 | 1272AAC | 0,0,255 | 1 | 0.084 | 0.5926 | 6.994 | 0.254 | 1.837 | 3.056 | 0 | 1014 | 1014 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.32 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1535 | 1535 | 0
25 | 1272ACSR | 255,255,0 | 0 | 0.085008 | 0.37171 | 0 | 0 | 0 | 0 | 1.382 | 1200 | 1440 | Bare | 1.382 | 7.297 | 1.382 | 1.382 | 1.382 | 1.382 | 7.297 | 8 | 81.41 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1200 | 1440 | 0
26 | 1351AAC | 0,255,255 | 0 | 0.086592 | 0.38174 | 0 | 0 | 0 | 0 | 1.37 | 1180 | 1410 | Bare | 1.37 | 7.2336 | 1.37 | 1.37 | 1.37 | 1.37 | 7.2336 | 8 | 59.44 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1180 | 1410 | 0
27 | 1351ACSR | 255,0,255 | 0 | 0.080256 | 0.36854 | 0 | 0 | 0 | 0 | 1.424 | 1250 | 1500 | Bare | 1.424 | 7.5187 | 1.424 | 1.424 | 1.424 | 1.424 | 7.5187 | 8 | 86.46 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1250 | 1500 | 0
28 | 1431AAC | 125,125,0 | 0 | 0.082368 | 0.37752 | 0 | 0 | 0 | 0 | 1.42 | 1220 | 1460 | Bare | 1.42 | 7.4976 | 1.42 | 1.42 | 1.42 | 1.42 | 7.4976 | 8 | 62.96 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1220 | 1460 | 0
29 | 1431ACSR | 0,125,125 | 0 | 0.075504 | 0.36485 | 0 | 0 | 0 | 0 | 1.465 | 1300 | 1560 | Bare | 1.465 | 7.7352 | 1.465 | 1.465 | 1.465 | 1.465 | 7.7352 | 8 | 91.58 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1300 | 1560 | 0
30 | 1510AAC | 125,0,125 | 0 | 0.078672 | 0.37488 | 0 | 0 | 0 | 0 | 1.47 | 1260 | 1510 | Bare | 1.47 | 7.7616 | 1.47 | 1.47 | 1.47 | 1.47 | 7.7616 | 8 | 66.44 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1260 | 1510 | 0
31 | 1510ACSR | 255,0,0 | 0 | 0.071808 | 0.36168 | 0 | 0 | 0 | 0 | 1.506 | 1340 | 1600 | Bare | 1.506 | 7.9517 | 1.506 | 1.506 | 1.506 | 1.506 | 7.9517 | 8 | 66.4 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1340 | 1600 | 0
32 | 1590AAC | 0,255,0 | 0 | 0.074976 | 0.37066 | 0 | 0 | 0 | 0 | 1.52 | 1300 | 1560 | Bare | 1.52 | 8.0256 | 1.52 | 1.52 | 1.52 | 1.52 | 8.0256 | 8 | 69.96 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1300 | 1560 | 0
33 | 1590ACSR | 0,0,255 | 0 | 0.068112 | 0.35851 | 0 | 0 | 0 | 0 | 1.545 | 1380 | 1650 | Bare | 1.545 | 8.1576 | 1.545 | 1.545 | 1.545 | 1.545 | 8.1576 | 8 | 101.76 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1380 | 1650 | 0
34 | 1AL | 125,0,0 | 1 | 1.223 | 0.77 | 5.351 | 1.817 | 2.371 | 2.638 | 0 | 162 | 181 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.82 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 238 | 264 | 0
35 | 1CN15 | 0,125,0 | 1 | 1.28 | 0.529 | 71.93 | 2.756 | 1.293 | 71.93 | 0 | 141 | 141 | ActZ | 0 | 0 | 0.75 | 1.08 | 0.289 | 0.0641 | 21.78 | 10 | 3.94 | Al | XLP | PVC | 90 | 0.289 | 1 | 0.05 | 0.06 | 0.985 | 1.2 | 0 |  | 161 | 161 | 0
36 | 1CN25 | 0,0,125 | 1 | 1.28 | 0.529 | 71.93 | 2.756 | 1.293 | 71.93 | 0 | 143 | 143 | ActZ | 0 | 0 | 0.9 | 1.21 | 0.289 | 0.0641 | 21.78 | 10 | 3.94 | Al | XLP | PVC | 90 | 0.1093 | 7 | 0.045 | 0.065 | 1.1 | 1.2 | 0 |  | 163 | 163 | 0
37 | 1CU | 255,255,0 | 1 | 0.765 | 0.77 | 5.352 | 1.304 | 2.287 | 2.638 | 0 | 217 | 241 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.25 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 304 | 343 | 0
38 | 1STCU | 0,255,255 | 1 | 0.773 | 0.7673 | 5.378 | 1.367 | 2.502 | 2.653 | 0 | 217 | 241 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.25 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 304 | 343 | 0
39 | 2/0AAC | 255,0,255 | 1 | 0.769 | 0.7253 | 5.693 | 1.363 | 2.46 | 2.738 | 0 | 243 | 243 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.67 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 357 | 357 | 0
40 | 2/0ACSR | 125,125,0 | 1 | 0.843 | 0.8479 | 4.861 | 1.323 | 2.366 | 2.505 | 0 | 241 | 241 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.01 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 355 | 355 | 0
41 | 2/0AL | 0,125,125 | 1 | 0.883 | 1.716 | 94.087 | 0.458 | 0.5 | 94.087 | 0 | 165 | 185 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.27 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 208 | 232 | 0
42 | 2/0CU | 125,0,125 | 1 | 0.481 | 0.742 | 5.558 | 1.02 | 2.259 | 2.695 | 0 | 287 | 319 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.94 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 405 | 450 | 0
43 | 2/0STCU | 255,0,0 | 1 | 0.487 | 0.739 | 5.587 | 1.08 | 2.474 | 2.709 | 0 | 287 | 319 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.94 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 405 | 450 | 0
44 | 2_1000CUEPR_PER_PHASE | 0,125,125 | 1 | 0.9 | 0.165 | 500.9 | 0.3 | 0.161 | 500.9 | 0 | 1000 | 1000 | ActZ | 0 | 0 | 1.652 | 1.8 | 1.152 | 0.0808 | 8.712 | 14 | 74.71 | Cu | EPR | PVC | 90 | 0.128 | 61 | 0.045 | 0.06 | 1.7 | 1.2 | 0 | double conductors 1000 CU | 1000 | 1000 | 0
45 | 211ACSR | 0,0,255 | 0 | 0.38491 | 0.46464 | 0 | 0 | 0 | 0 | 0.642 | 460 | 550 | Bare | 0.642 | 3.3898 | 0.642 | 0.642 | 0.642 | 0.642 | 3.3898 | 8 | 17.024 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 460 | 550 | 0
46 | 250CU | 0,255,0 | 1 | 0.26 | 0.691 | 5.973 | 0.799 | 2.208 | 2.847 | 0 | 431 | 479 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.68 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 640 | 678 | 0
47 | 266AAC | 0,255,0 | 0 | 2.0291 | 3.6443 | 0 | 0 | 0 | 0 | 0.63 | 377 | 377 | Bare | 0.63 | 3.3264 | 0.63 | 0.63 | 0.63 | 0.63 | 3.3264 | 8 | 11.7 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.189 | 0.087 | 1.228 | 1 | 0 |  | 555 | 555 | 0
48 | 266ACSR | 0,0,255 | 0 | 0.38491 | 0.46464 | 0 | 0 | 0 | 0 | 0.642 | 460 | 550 | Bare | 0.642 | 3.3898 | 0.642 | 0.642 | 0.642 | 0.642 | 3.3898 | 8 | 17.024 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 460 | 550 | 0
49 | 2A | 0,0,255 | 1 | 0.979 | 0.802 | 5.137 | 1.516 | 2.328 | 2.577 | 0 | 184 | 205 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.96 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 258 | 287 | 0
50 | 2ACSR | 0,125,0 | 1 | 1.583 | 0.872 | 4.725 | 2.177 | 2.607 | 2.464 | 0 | 161 | 161 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.99 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 241 | 241 | 0
51 | 2AL | 0,0,125 | 1 | 1.542 | 0.784 | 5.254 | 2.163 | 2.484 | 2.611 | 0 | 148 | 165 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.83 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 209 | 233 | 0
52 | 2CN15 | 255,255,0 | 1 | 1.606 | 0.541 | 74.187 | 3.006 | 1.154 | 74.187 | 0 | 123 | 123 | ActZ | 0 | 0 | 0.77 | 1.08 | 0.283 | 0.0641 | 21.788 | 10 | 3.12 | Al | XLP | PVC | 90 | 0.0974 | 7 | 0.045 | 0.065 | 0.98 | 1.2 | 0 |  | 141 | 141 | 0
53 | 2CN25 | 0,255,255 | 1 | 1.606 | 0.541 | 74.187 | 3.006 | 1.154 | 74.187 | 0 | 123 | 123 | ActZ | 0 | 0 | 0.85 | 1.2 | 0.283 | 0.0641 | 21.78 | 10 | 3.12 | Al | XLP | PVC | 90 | 0.0974 | 7 | 0.045 | 0.065 | 1.1 | 1.2 | 0 |  | 141 | 141 | 0
54 | 2CU | 255,0,255 | 1 | 0.956 | 0.7879 | 5.235 | 1.559 | 2.701 | 2.613 | 0 | 197 | 197 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.96 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 280 | 280 | 0
55 | 2CW | 125,0,0 | 1 | 0.979 | 0.799 | 5.162 | 1.573 | 2.534 | 2.592 | 0 | 204 | 205 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.07 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 300 | 0
56 | 2STCU | 125,125,0 | 1 | 0.975 | 0.7813 | 5.28 | 1.578 | 2.694 | 2.626 | 0.2922 | 185 | 205 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.96 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 258 | 287 | 0
57 | 3/0AAC-GIS | 0,125,125 | 1 | 0.61 | 0.714 | 5.781 | 1.113 | 2.198 | 2.755 | 0 | 252 | 280 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.67 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 368 | 409 | 0
58 | 3/0AL | 0,125,125 | 1 | 0.61 | 0.714 | 5.781 | 1.113 | 2.198 | 2.755 | 0 | 252 | 280 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.67 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 368 | 409 | 0
59 | 3/0CU | 125,0,125 | 1 | 0.3825 | 0.729 | 5.663 | 0.92 | 2.245 | 2.724 | 0 | 332 | 369 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.54 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 470 | 522 | 0
60 | 3/0STCU | 255,0,0 | 1 | 0.386 | 0.725 | 5.696 | 0.866 | 2.243 | 2.739 | 0 | 369 | 369 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.54 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 552 | 522 | 0
61 | 3_RUNS_556AAC | 0,125,125 | 1 | 0.062 | 0.2152 | 2.1363 | 0.2217 | 0.7213 | 0.973 | 0 | 1830 | 1875 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.08 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2700 | 2700 | 0
62 | 336AAC | 0,255,0 | 1 | 0.305 | 0.6761 | 6.115 | 0.785 | 2.194 | 2.846 | 0 | 452 | 452 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.39 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 676 | 676 | 0
63 | 336AAC_SC | 0,255,0 | 1 | 0.306 | 0.46 | 8.932 | 1.11 | 1.947 | 3.317 | 0 | 452 | 452 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.39 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 676 | 676 | 0
64 | 336ACSR | 0,0,255 | 1 | 0.303 | 0.6699 | 6.172 | 0.782 | 2.188 | 2.861 | 0 | 451 | 451 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.3 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 671 | 671 | 0
65 | 336ACSR100C | 125,0,0 | 1 | 0.303 | 0.673 | 2.849 | 0.805 | 2.157 | 6.141 | 0 | 504 | 560 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.3 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 655 | 728 | 0
66 | 336ACSR2P | 0,125,0 | 1 | 0.285 | 0.357 | 11.551 | 0.595 | 1.493 | 3.759 | 0 | 810 | 902 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.6 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1206 | 1342 | 0
67 | 350CN15 | 0,0,125 | 1 | 0.381 | 0.42 | 126.02 | 1.316 | 0.546 | 126.02 | 0 | 317 | 317 | ActZ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.46 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 363 | 363 | 0
68 | 350CN25 | 0,0,125 | 1 | 0.381 | 0.42 | 126.02 | 1.316 | 0.546 | 126.02 | 0 | 317 | 317 | ActZ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.46 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 363 | 363 | 0
69 | 350CN35 | 0,0,125 | 1 | 0.381 | 0.42 | 126.02 | 1.316 | 0.546 | 126.02 | 0 | 317 | 317 | ActZ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.46 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 363 | 363 | 0
70 | 350CU | 0,125,0 | 1 | 0.9847 | 3.5577 | 6.101 | 0.708 | 2.1938 | 2.881 | 0.679 | 594 | 594 | Bare | 0.244 | 0.3062 | 1 | 1.3 | 0.9 | 0.1 | 0.7001 | 8 | 15 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.189 | 0.087 | 1.228 | 1 | 0 |  | 841 | 841 | 0
71 | 3C1PILC | 255,255,0 | 1 | 1.28 | 0.529 | 71.93 | 2.756 | 1.293 | 71.93 | 0 | 170 | 170 | ActZ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.94 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 170 | 170 | 0
72 | 3C350PILC | 0,255,255 | 1 | 0.381 | 0.42 | 126.02 | 1.316 | 0.546 | 126.02 | 0 | 494 | 494 | ActZ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.46 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 494 | 494 | 0
73 | 4/0 AAC | 125,125,125 | 1 | 0.484 | 0.6969 | 5.93 | 0.964 | 2.215 | 2.799 | 0 | 326 | 329 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 479 | 481 | 0
74 | 4/0AAC | 125,125,125 | 1 | 0.484 | 0.6969 | 5.93 | 0.964 | 2.215 | 2.799 | 0 | 326 | 329 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 479 | 481 | 0
75 | 4/0AAC_SC | 125,125,125 | 1 | 0.485 | 0.481 | 8.544 | 1.289 | 1.968 | 3.22 | 0 | 326 | 329 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 479 | 481 | 0
76 | 4/0AAC-GIS | 125,125,125 | 1 | 0.484 | 0.6969 | 5.93 | 0.964 | 2.215 | 2.799 | 0 | 326 | 329 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 479 | 481 | 0
77 | 4/0ACSR | 255,0,255 | 1 | 0.573 | 0.7911 | 5.214 | 1.053 | 2.309 | 2.607 | 0 | 314 | 345 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.91 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 465 | 465 | 0
78 | 4/0CN15 | 125,125,0 | 1 | 0.452 | 0.398 | 116.152 | 0.941 | 0.317 | 116.152 | 0 | 265 | 265 | ActZ | 0 | 0 | 1.03 | 1.32 | 0.522 | 0.0641 | 13.88 | 11 | 9.94 | Al | XLP | PVC | 90 | 0.1739 | 7 | 0.045 | 0.06 | 1.1 | 1.2 | 0 |  | 302 | 302 | 0
79 | 4/0CN25 | 0,125,125 | 1 | 0.452 | 0.398 | 116.152 | 0.941 | 0.317 | 116.152 | 0 | 267 | 267 | ActZ | 0 | 0 | 1.03 | 1.32 | 0.522 | 0.0641 | 13.88 | 11 | 9.94 | Al | XLP | PVC | 90 | 0.1739 | 7 | 0.045 | 0.06 | 1.1 | 1.2 | 0 |  | 304 | 304 | 0
80 | 4/0CU | 125,0,125 | 1 | 0.257 | 0.697 | 5.92 | 0.795 | 2.214 | 2.792 | 0 | 405 | 477 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.81 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 597 | 687 | 0
81 | 4/0CUEPR15_Triplex | 0,125,0 | 1 | 0.32 | 0.218 | 133.234 | 0.88 | 0.293 | 133.234 | 1.2 | 300 | 300 | ActZ | 0 | 0 | 1 | 1.21 | 0.527 | 0.0641 | 13.89 | 20 | 15.9 | Cu | XLP | PVC | 90 | 0.1322 | 19 | 0.189 | 0.087 | 1.65 | 1.2 | 0 |  | 300 | 300 | 0
82 | 4A | 255,0,0 | 1 | 1.545 | 0.831 | 4.959 | 2.154 | 2.534 | 2.525 | 0 | 143 | 168 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 204 | 240 | 0
83 | 4ACSR | 0,255,0 | 1 | 2.459 | 0.8625 | 4.777 | 3.062 | 2.775 | 2.48 | 0 | 121 | 133 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.14 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 176 | 195 | 0
84 | 4AWAC | 0,0,255 | 1 | 1.93 | 2.547 | 4.825 | 0.853 | 2.652 | 2.485 | 0 | 132 | 147 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.22 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 187 | 155 | 0
85 | 4BIRON | 125,0,0 | 1 | 12.87 | 3.811 | 1.075 | 13.243 | 6.006 | 8.686 | 0 | 21 | 21 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 30 | 30 | 0
86 | 4CU | 0,125,0 | 1 | 1.52 | 0.816 | 5.053 | 2.122 | 2.729 | 2.561 | 0 | 147 | 147 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 208 | 208 | 0
87 | 4CW | 0,0,125 | 1 | 4.573 | 0.816 | 5.053 | 5.176 | 2.729 | 2.561 | 0 | 102 | 121 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 240 | 0
88 | 4STCU | 255,255,0 | 1 | 1.55 | 0.8094 | 5.094 | 2.153 | 2.722 | 2.573 | 0 | 135 | 159 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 167 | 208 | 0
89 | 500AL | 0,0,125 | 0 | 0.226 | 0.1468 | 0 | 0 | 0 | 0 | 0.845 | 467 | 560 | Tape | 0.845 | 4.4616 | 0.845 | 0.845 | 0.845 | 0.845 | 4.4616 | 8 | 22 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.189 | 0.087 | 1.228 | 1 | 0 |  | 467 | 560 | 0
90 | 500CU | 0,255,255 | 1 | 0.132 | 0.655 | 6.305 | 0.67 | 2.172 | 2.89 | 0 | 613 | 722 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.35 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 898 | 1057 | 0
91 | 500CUEPR15_Triplex | 0,125,0 | 1 | 0.145 | 0.234 | 279.687 | 0.701 | 0.31 | 279.687 | 1.2 | 400 | 400 | ActZ | 0 | 0 | 1.5 | 1.9 | 0.811 | 0.0641 | 13.89 | 20 | 30.7 | Cu | XLP | PVC | 90 | 0.1622 | 19 | 0.06 | 0.08 | 1.65 | 1.2 | 0 |  | 400 | 400 | 0
92 | 500PILC | 255,0,255 | 1 | 0.131 | 0.418 | 126.928 | 0.348 | 1.161 | 126.928 | 0 | 686 | 686 | ActZ | 0 | 0 | 1.5 | 1.9 | 0.811 | 0 | 0 | 0 | 30.7 | Cu | XLP | PVC | 90 | 0.1622 | 19 | 0.075 | 0.1 | 1.7 | 1.2 | 0 |  | 686 | 686 | 0
93 | 500VIFC | 125,125,0 | 1 | 0.131 | 0.418 | 126.928 | 0.348 | 1.161 | 126.928 | 0 | 686 | 686 | ActZ | 0 | 0 | 1.5 | 1.9 | 0.811 | 0 | 0 | 0 | 30.7 | Cu | XLP | PVC | 90 | 0.1622 | 19 | 0.075 | 0.1 | 1.7 | 1.2 | 0 |  | 686 | 686 | 0
94 | 556AAC | 0,125,125 | 1 | 0.186 | 0.6456 | 6.409 | 0.665 | 2.164 | 2.919 | 0 | 610 | 625 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.08 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 913 | 913 | 0
95 | 556AAC_SC | 0,125,125 | 1 | 0.186 | 0.429 | 9.582 | 0.991 | 1.916 | 3.478 | 0 | 482 | 691 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.08 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 793 | 915 | 0
96 | 556ACSR | 0,125,125 | 1 | 0.1817 | 0.6277 | 6.595 | 0.661 | 2.146 | 2.964 | 0 | 617 | 617 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.08 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 907 | 907 | 0
97 | 6A | 125,0,125 | 1 | 2.44 | 0.859 | 4.8 | 3.05 | 2.753 | 2.48 | 0 | 108 | 128 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.96 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 128 | 150 | 0
98 | 6AL | 255,0,0 | 1 | 3.898 | 0.841 | 4.898 | 4.453 | 2.891 | 2.507 | 0 | 88 | 88 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 129 | 129 | 0
99 | 6AMER | 0,255,0 | 1 | 5.437 | 0.82 | 2.544 | 5.939 | 2.943 | 5.024 | 0 | 97 | 114 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 128 | 150 | 0
100 | 6CR | 0,0,255 | 1 | 12.87 | 3.811 | 1.075 | 13.243 | 6.006 | 8.683 | 0 | 18 | 18 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 25 | 0
101 | 6CU | 125,0,0 | 1 | 2.417 | 0.8441 | 4.882 | 3.02 | 2.757 | 2.512 | 0.162 | 110 | 110 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.96 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 156 | 156 | 0
102 | 6CW | 0,125,0 | 1 | 7.204 | 0.8442 | 4.882 | 7.807 | 2.757 | 2.511 | 0 | 45 | 45 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 65 | 65 | 0
103 | 6IRON | 0,0,125 | 1 | 14.63 | 0.8441 | 4.883 | 15.233 | 2.757 | 2.512 | 0 | 14 | 14 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 20 | 0
104 | 6STCU | 255,255,0 | 1 | 2.417 | 0.847 | 4.86 | 3.029 | 2.738 | 2.5 | 0 | 100 | 118 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.96 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 133 | 156 | 0
105 | 6STEL | 0,255,255 | 1 | 16.994 | 0.8 | 1.075 | 17.597 | 2.757 | 8.683 | 0 | 13 | 13 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 18 | 0
106 | 6WP | 255,0,255 | 1 | 2.417 | 0.847 | 4.86 | 3.029 | 2.738 | 2.496 | 0 | 102 | 120 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.96 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 133 | 156 | 0
107 | 716STEEL | 125,125,0 | 1 | 12.87 | 3.811 | 1.075 | 13.243 | 6.006 | 8.683 | 0 | 70 | 70 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 100 | 0
108 | 750CN15 | 0,125,125 | 1 | 0.27 | 0.326 | 182.6 | 0.68 | 0.253 | 182.6 | 0 | 479 | 479 | ActZ | 0 | 0 | 1.48 | 1.92 | 0.974 | 0.064 | 13.9 | 18 | 35.28 | Al | XLP | PVC | 90 | 0.1109 | 61 | 0.05 | 0.15 | 1.57 | 1.2 | 0 |  | 548 | 548 | 0
109 | 750CUEPR | 125,0,125 | 1 | 0.206 | 0.345 | 288.5 | 0.624 | 0.333 | 288.5 | 0 | 665 | 665 | ActZ | 0 | 0 | 1.48 | 1.92 | 0.974 | 0.064 | 13.9 | 18 | 56.03 | Cu | EPR | PVC | 90 | 0.1109 | 61 | 0.05 | 0.15 | 1.57 | 1.2 | 0 |  | 758 | 758 | 0
110 | 750CUEPR - 4 RUNS | 125,0,125 | 1 | 0.0515 | 0.0863 | 1000 | 0.156 | 0.0833 | 1000 | 0 | 2660 | 2660 | ActZ | 0 | 0 | 1.48 | 1.92 | 0.974 | 0.064 | 13.9 | 18 | 56.03 | Cu | EPR | PVC | 90 | 0.1109 | 61 | 0.05 | 0.15 | 1.57 | 1.2 | 0 | 4 runs of 750 copper | 3032 | 3032 | 0
111 | 750CUEPR_SPG | 255,0,0 | 1 | 0.09 | 0.393 | 179.7 | 0.248 | 1.121 | 179.7 | 0 | 682 | 682 | ActZ | 0 | 0 | 1.48 | 1.92 | 0.974 | 0 | 0 | 0 | 56.03 | Cu | EPR | PVC | 90 | 0.1109 | 61 | 0.05 | 0.15 | 1.5 | 1.2 | 0 |  | 682 | 682 | 0
112 | 750CUXLP | 0,255,0 | 1 | 0.206 | 0.345 | 288.5 | 0.624 | 0.333 | 288.5 | 0 | 665 | 665 | ActZ | 0 | 0 | 1.48 | 1.92 | 0.974 | 0.0641 | 13.9 | 18 | 56.03 | Cu | XLP | PVC | 90 | 0.1109 | 61 | 0.05 | 0.15 | 1.5 | 1.2 | 0 |  | 758 | 758 | 0
113 | 750CUXLP_SPG | 0,0,255 | 1 | 0.09 | 0.393 | 179.7 | 0.248 | 1.121 | 179.7 | 0 | 682 | 682 | ActZ | 0 | 0 | 1.48 | 1.92 | 0.974 | 0 | 0 | 0 | 56.03 | Cu | XLP | PVC | 90 | 0.1109 | 61 | 0.05 | 0.15 | 1.5 | 1.2 | 0 |  | 682 | 682 | 0
114 | 795 AAC | 255,0,0 | 0 | 0.1415 | 0.41448 | 0 | 0 | 0 | 0 | 1.026 | 840 | 1000 | Bare | 1.026 | 5.4173 | 1.026 | 1.026 | 1.026 | 1.026 | 5.4173 | 8 | 34.98 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 840 | 1000 | 0
115 | 795 ACSR | 0,255,0 | 0 | 0.13728 | 0.40075 | 0 | 0 | 0 | 0 | 1.093 | 900 | 1080 | Bare | 1.093 | 5.771 | 1.093 | 1.093 | 1.093 | 1.093 | 5.771 | 8 | 50.9 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 900 | 1080 | 0
116 | 795AAC | 125,0,0 | 1 | 0.131 | 0.626 | 6.61 | 0.634 | 2.11 | 2.97 | 0 | 762 | 806 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.82 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1146 | 1146 | 0
117 | 795ACSR | 0,125,0 | 1 | 0.128 | 0.6057 | 6.839 | 0.41 | 1.901 | 3.021 | 0 | 711 | 711 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.82 | Al | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1134 | 1134 | 0
118 | 7S8CU | 0,0,125 | 1 | 0.553 | 0.7471 | 5.525 | 1.156 | 2.66 | 2.693 | 0 | 292 | 305 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.63 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 409 | 409 | 0
119 | 8A | 255,255,0 | 1 | 3.87 | 0.882 | 4.665 | 4.424 | 2.929 | 2.437 | 0 | 70 | 70 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.23 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 95 | 95 | 0
120 | 8AMER | 0,255,255 | 1 | 8.753 | 0.845 | 4.872 | 9.185 | 3.3031 | 2.5 | 0 | 70 | 70 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 95 | 95 | 0
121 | 8CR | 255,0,255 | 1 | 19.8 | 3.811 | 1.075 | 19.55 | 6.031 | 8.683 | 0 | 13 | 13 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 18 | 18 | 0
122 | 8CU | 125,125,0 | 1 | 3.841 | 0.8723 | 4.723 | 4.444 | 2.785 | 2.464 | 0 | 82 | 82 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 115 | 115 | 0
123 | 8CW | 0,125,125 | 1 | 11.391 | 0.8723 | 4.723 | 11.994 | 2.785 | 2.464 | 0 | 30 | 30 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.41 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 40 | 40 | 0
124 | 8STCU | 0,128,128 | 1 | 11.3911 | 0.87226 | 4.723 | 11.994 | 2.7852 | 2.4642 | 1.2 | 51 | 60 | Bare | 0.244 | 0.30624 | 1 | 1.3 | 0.9 | 0.1 | 0.70013 | 8 | 0.41 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.189 | 0.087 | 1.228 | 1 | 0 |  | 72 | 85 | 0
125 | 9/19STR | 125,0,125 | 1 | 5.42 | 0.923 | 4.46 | 5.919 | 3.042 | 2.373 | 0 | 70 | 70 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 70 | 70 | 0
126 | 900 ACSR | 255,0,255 | 0 | 0.11827 | 0.39283 | 0 | 0 | 0 | 0 | 1.162 | 970 | 1160 | Bare | 1.162 | 6.1354 | 1.162 | 1.162 | 1.162 | 1.162 | 6.1354 | 8 | 57.6 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 970 | 1160 | 0
127 | 900 CU | 125,125,0 | 0 | 0.074976 | 0.4055 | 0 | 0 | 0 | 0 | 1.092 | 1220 | 1460 | Bare | 1.092 | 5.7658 | 1.092 | 1.092 | 1.092 | 1.092 | 5.7658 | 8 | 60.75 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 1220 | 1460 | 0
128 | 91/2D | 125,0,125 | 1 | 5.42 | 0.923 | 4.46 | 5.919 | 3.042 | 2.373 | 0 | 50 | 50 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 70 | 70 | 0
129 | Cable 12.5kV direct burial | 255,0,0 | 0 | 0 | 0.1 | 0 | 0 | 0.1 | 0 | 1.2 | 100 | 110 | Bare | 0.244 | 0.306 | 1 | 1.3 | 0.9 | 0.1 | 0.7 | 8 | 15 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.18898 | 0.086614 | 1.2283 | 1 | 0 |  | 100 | 110 | 0
130 | Low Impedance Bus | 0,125,0 | 1 | 0.005 | 0.005 | 0 | 0.005 | 0.005 | 0 | 1.2 | 5000 | 5000 | ActZ | 0.244 | 0.306 | 1 | 1.3 | 0.9 | 0.1 | 0.7 | 8 | 15 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.189 | 0.087 | 1.228 | 1 | 0 |  | 5000 | 5000 | 0
131 | REACTOR | 255,0,0 | 1 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 400 | 400 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.14 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 400 | 400 | 0
132 | UNK | 255,0,0 | 1 | 2.523 | 0.866 | 4.756 | 3.13 | 2.773 | 2.465 | 0 | 10 | 10 | Bare | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.14 | Cu | XLP | PVC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10 | 10 | 0
133 | UNK UND | 0,125,0 | 1 | 2.523 | 0.866 | 4.756 | 3.13 | 2.773 | 2.465 | 1.2 | 10 | 10 | Conc | 0.244 | 0.306 | 1 | 1.3 | 0.9 | 0.1 | 0.7 | 8 | 15 | Cu | XLP | PVC | 90 | 0.1322 | 50 | 0.189 | 0.087 | 1.228 | 1 | 0 |  | 10 | 10 | 0